## Slide 1
Solar Heat for Industrial Processes Webinar series #3 - Fresnel Collector Technology
Irapua Ribeiro
17.06.2021

## Slide 2
Fresnel Collector technology

## Slide 3
Fresnel Collector technology
Generates heat up to 400 °C and 120 bar
Produces steam, heat up water or thermal oil
System lifetime: + 25 years
Modular design, easily expandable
Lightweight structure allows rooftop installation
27 kg/m²
Uniaxially tracked mirrors concentrate sunlight onto an absorber where heat is generated

## Slide 4
Fresnel Collector – Components
Mirror system (robust)
Support Structure (lightweight)
Absorber tube (high efficiency)
Control system (smart control)

## Slide 5
Fresnel Collector – Technology overview
Higher ground usage factor ~65% higher space efficiency (mirror area / ground area)
Space needs: 1 MWth uses ~ 3000 m²
Low wind load Low exposure to wind  less structural loads
Good weight distribution Even distribution of the weight on the ground
Automatic operation, from sunrise to sunset Cleaning designs: automatic or manual
Low dust accumulation: stow position (e.g., 18h to 6h), self cleaning

## Slide 6
Fresnel System – Steam generation concept

## Slide 7
Fresnel System – Steam drum
Large pressure vessel
mainly filled with liquid water (80% of volume)
partly filled with steam (20% of volume)
Additional Functions of Storage
Two-phase separation
Expansion Vessel
Steam pressurization
Blow-down
De-Aeration
Anti-Freeze protection
Fresnel collector field
Industrial processes

## Slide 8
Fresnel System – Steam drum

## Slide 9
Fresnel System – Operation Diagram
Data Center
Very stable pressure in steam network due to solar generated steam
Fluctuating DNI
Fluctuating Pressure in Drum
T collector out determined by steam drum pressure
Steam valve opening controls pressure in steam network
Without irradiation the fossil boiler provides steam

## Slide 10
Fresnel System - Applications
Food & Beverage | Pasteurization / Blanching / Distillation / Cleaning
Textile | Dyeing / Drying / Washing
Pharma | Sterilization / Injection molding / Distillation
Paper | Bleaching / Cooking / Drying
Automotive | Drying / Electroplating / Blueing
Oil & Chemical | Distillation / EOR
Several industrial applications
Large energy requirements

## Slide 11
Demo site at RAR
RAR Açúcar is a company dedicated to the refining and selling of sugar
Solar steam will reduce fuel consumption and avoid emissions from burning fuel oil and natural gas
Heating
Sugar crystallization process: 125°C
Solar steam operation modes:
  Main use: 1 bar(g) grid for all major processes and the degasser
  Optional: 5 bar(g) grid used for cleaning (in continuous process)
NEEDS

## Slide 12
Demo site at RAR
Technology: Solar Fresnel Collectors
Solar field: 30 modules
Orientation: 47° from the N-S-axis
660 m² aperture area
Production: steam @10 bar
Under execution

## Slide 13
Demo site at RAR – System layout
30 modules (15 strings of 2 modules each) | 
690 m² aperture area | 
415 kW thermal power at reference conditions | 
926 m² ground space (15,2m x 60,9m) | 
+ access space of 1,5 m each side | 
75 % ground space efficiency | 

## Slide 14
Demo site at RAR – Roof installation

## Slide 15
Demo site at RAR – BOP container
Steam storage and BOP Container
Replicability
Reduced costs (engineering, planning)
Pre-manufacturing & tests before shipping
Reduced installation time onsite
Short pipe ways from solar field to solar BoP
Clear definition of solar system interfaces
Storage capacity: 60 minutes and 415 kWh (1,5 GJ)

## Slide 16
Demo site at RAR – Steam integration
Existing Steam Network
Solar Steam Boiler

## Slide 17
Control Tool Framework modules related to plant
Industrial process
17
CHP
Weather forecast
TES
Solar thermal
A) Control of solar thermal plant
Goal: stable temperature
Industrial process
17
CHP
Weather forecast
TES
Solar thermal
A) Control of solar thermal plant
Goal: stable temperature
17
CHP
Weather forecast
TES
Solar thermal
Industrial process
A) Control of solar thermal plant
Goal: stable temperature
Goal: future heat forecast
Industrial process
17
CHP
Weather forecast
TES
Solar thermal
A) Control of solar thermal plant
Goal: stable temperature
17
CHP
Weather forecast
TES
Solar thermal
Industrial process
A) Control of solar thermal plant
Goal: stable temperature
Goal: future heat forecast
Rhyd,A >>
Rhyd,B <<
Goal: stable hydraulic condition
Industrial process
17
CHP
Weather forecast
TES
Solar thermal
A) Control of solar thermal plant
Goal: stable temperature
17
CHP
Weather forecast
TES
Solar thermal
Industrial process
A) Control of solar thermal plant
Goal: stable temperature
Goal: future heat forecast
Rhyd,A >>
Rhyd,B <<
Goal: stable hydraulic condition
Goal: optimal overall control
E) Distributed Learning
Features
Goal: efficient & smart monitoring

## Slide 18
What is the Replication Tool?
The Replication Tool is a software able to evaluate the techno-economic potential of SHIP solution, starting from local solar potential and current process heat demand.
It gives:
Evaluation of solar field parameters
Expected energetic and environmental results
Preliminary economic figures.
Contact us if you want to receive a free assessment: info@ship2fair-h2020.eu

## Slide 19
info@ship2fair-h2020.eu
www.ship2fair-h2020.eu
Thank you!